## Slide 1: PLC The microprocessor-based controller uses a programmable memory to store instructions and to implement functions such as logic, sequencing, timing, counting and arithmetic to control machines and processes designed to be operated by engineers. OR is a type of industrial computer that controls and monitors machines and processes. PLCs are used in manufacturing to control activities like assembly lines, robotic devices, and machines. The first PLC was introduced in 1969
.

## Slide 2
PLC
outputs
Inputs
Program

## Slide 3: PLC GREATEST ADVANTAGE
The same basic controller can be used with various control systems.
To modify a control system there is no need to rewire.
Results are flexible and cost-effective.

## Slide 4: PLC FEATURES
Rugged and designed to withstand temperature, vibrations, humidity and noise.
Have an interface for input and outputs already inside the controller.
Easily programmed and easily understood programming language which is primarily concerned with logic and switching.

## Slide 5: PLC VS OTHER COMPUTERS
PLC | COMPUTER
Optimized for control tasks and industrial environment. | Optimized for calculation and display tasks.

## Slide 6
Processor
Programming Device
Program &Data Memory
Communication
Interface
Input interface
Output interface
Power supply
PLC SYSTEM

## Slide 7: PLC SYSTEM
Processor – interprets input and carries out control actions.
Power – convert AC to DC or Rectification.
Programming device –used to enter the required program into the memory of the processor [program developed in the device and transferred to the memory unit of the PLC].
Memory unit - where the program is stored that is used to control actions to be executed by the microprocessor.

## Slide 8: PLC SYSTEM
Input/Output – Input and output signals can be classified as
Discrete signal.
Digital signal.
Analogue signal.

## Slide 9
Discrete Signal
Devices giving discrete or digital signals are ones where the signals are either off or on. Thus a switch is a device giving a discrete signal, either no voltage or a voltage
Voltage
Time

## Slide 10
Digital signal
Digital devices can be considered to be essentially discrete devices which give a sequence of on−off signals
Voltage
Time

## Slide 11
Analogue signal
Analogue devices give signals whose size is proportional to the monitored variable. For example, a temperature sensor may give a voltage proportional to the temperature.
Voltage
Time

## Slide 12
Communication interface
Used to receive and transmit data on communication networks from or to other remote PLCs.
Concerned with device verification, data acquisition, and synchronisation between user applications and connection management.

## Slide 13: Basic communication model
Supervisory System
PLC1
PLC2
Machine/Plant
Machine/Plant

## Slide 14: PLC INTERNAL ARCHTECTURE
User program RAM
CPU
Clock
System ROM
Data RAM
Input/
Output Unit
Battery
Address bus
Control bus
Data bus
Program panel
Input/Output system bus
Buffer
Latch
Optocoupler
Driver Interface
Driver

## Slide 15: PLC INTERNAL ARCHTECTURE
PLC CPU
Operates between 1 to 8 MHz
Frequency determines operation speed of PLC and provide timing and synchronisation for all elements in the system.
CPU performs Arithmetic Logic unit ALU [OR NOT AND OR XOR].
CPU control unit is used to control the timing of operations.
CPU termed register used to store information involved in program execution.

## Slide 16: PLC INTERNAL ARCHTECTURE
PLC BUS
Data bus – Carries data used in processing carried out by CPU .
Address bus – carries address of memory location.
Control bus - Carries information used by PLC for control actions.
System bus – For communications between input output ports and input output units.
.

## Slide 17: PLC INTERNAL ARCHTECTURE
MEMORY
Read Only Memory ROM Permanent storage for operating system and fixed data used by PLC.
Random Access Memory RAM For user program.
Data RAM where information is stored on the status of input and output devices and the values of timers and counters and other internal devices.
EPROM Erasable and programmable ROM - programmed and the program is made permanent.

## Slide 18: INPUT/ OUTPUT
The input/output channels provide isolation and signal conditioning functions so that sensors and actuators can often be directly connected to them without the need for other circuitry. Electrical isolation from the external world is usually by means of optoisolators (the term optocoupler is also often used).
PLC INTERNAL ARCHTECTURE

## Slide 19
Light
Emitting
Diode
Photo
Transistor
Infrared radiation
OPTOISOLATORS | OPTOCOUPLER

## Slide 20
OUTPUT LEVELS
Input
channel
Inputs digital
signal levels
5V
24V
110V
240V
To input
output unit
5V
Digital signal
level
A range of inputs might be available with a larger PLC, e.g. 5 V, 24 V, 110 V and 240 V digital/discrete, i.e. on−off, signals. A small PLC is likely to have just one form of input, e.g. 24 V.

## Slide 21
OUTPUT LEVELS
output
channel
24V 1mA DC
110V 1A DC
240V 1A AC
240V 2A AC
From input/
output unit
5V digital
Outputs
Switching
The output from the output channel might be a 24 V, 100 mA switching signal, a d.c. voltage of 110 V, 1 A or perhaps 240 V, 1 A a.c., or 240 V, 2 A a.c., from a triac output channel With a small PLC, all the outputs might be of one type, e.g. 240 V a.c., 1 A. With modular PLCs, however, a range of outputs can be accommodated by selection of the modules to be used

## Slide 22
OUTPUT TYPES
1. Relay types.
2. Transistor types.
3. Triac types.
Relay type
The signal from the PLC output is used to operate a relay and is able to switch currents of the order of a few amperes in an external circuit. The relay not only allows small currents to switch much larger currents but also isolates the PLC from the external circuit. Relays are, however, relatively slow to operate. Relay outputs are suitable for a.c. and d.c. switching. They can withstand high surge currents and voltage transients.

## Slide 23
OUTPUT TYPES
Transistor type
Output uses a transistor to switch current through the external circuit. This gives a considerably faster switching action. It is, however, strictly for d.c. switching and is destroyed by overcurrent and high reverse voltage. As a protection, either a fuse or built-in electronic protection are used. Optoisolators are used to provide isolation.
Triac type
with optoisolators for isolation, can be used to control external loads which are connected to the a.c. power supply. It is strictly for a.c. operation and is very easily destroyed by overcurrent. Fuses are virtually always included to protect such outputs.

## Slide 24
SOURCING
input
Module
(Current Source)
input
Module
Input
Device
Output
Load
an input device receives current from the input module, i.e. the input module is the source of the current. If the current flows from the output module to an output load then the output module is referred to as sourcing

## Slide 25
SINKING
input
Module
(Current Sink)
input
Module
Input
Device
Output
Load
an input device supplies current to the input module, i.e. the input module is the sink for the current If the current flows to the output module from an output load then the output module is referred to as sinking

## Slide 26
1.Hand-held programming device
programming devices will normally contain enough memory to allow the unit to retain programs while being carried from one place to another.
2. Desktop consoles
Are likely to have a visual display unit with a full keyboard and screen display.
PROGRAMMING A PLC

## Slide 27
3 Personal computers
Are widely configured as program development work-stations. Some PLCs only require the computer to have appropriate software; others require special communication cards to interface with the PLC. A major advantage of using a computer is that the program can be stored on the hard disk or a CD and copies easily made.
PROGRAMMING A PLC

## Slide 28
common types of mechanical design for PLC systems
1. single box type.
2. modular/rack type.
The single box type (or, as sometimes termed, brick) is commonly used for small programmable controllers and is supplied as an integral compact package complete with power supply, processor, memory, and input/output units. Typically such a PLC might have 6, 8, 12 or 24 inputs and 4, 8 or 16 outputs and a memory which can store some 300 to 1000 instructions.
Single box type.

## Slide 29
common types of mechanical design for PLC systems
consists of separate modules for power supply, processor, etc., which are often mounted on rails within a metal cabinet. Thus it is comparatively easy to expand the number of input/output (I/O) connections by just adding more input/output modules or to expand the memory by adding more memory units. An example of such a modular system is provided by the Allen-Bradley PLC-5 PLC of Rockwell automation.
modular/rack type.